# electrical-itp-template | Inspection and Test Plan

[Fill: project name] | Ordinary Low-Voltage Building Electrical Installation ITP — Editable Baseline — free editable baseline | [Fill: Australian state/territory] | Rev 00 | 2026-10-06 | For review

Contractor: [Fill: contractor]    Client: [Fill: client]
Scope: Original reusable baseline for ordinary low-voltage building electrical installation work such as general lighting, socket outlets, distribution boards and associated wiring. Excludes high voltage/network works, hazardous areas, solar PV/battery, fire detection, security/access control, lifts, specialist systems and temporary construction supplies unless separately scoped. This is an inspection plan, not an electrical design, certificate, licence or authorisation. This is a free, editable, proposed baseline and is not tailored to a project, approved by a client, or evidence of completed inspection. Before use, complete the scope questions and bracketed fields, confirm every criterion and control against current project documents, and remove non-applicable rows.
Exclusions: Confirm exclusions for this project; use the scope notes above.

| ID | Stage | Inspection / test | Method | Acceptance requirement | Reference | Frequency | Responsible role | Point | Approval / witness party | Notice / release | Record | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EL01 | Scope and regulatory basis | Proposed: baseline — Confirm circuits, areas, system boundaries, exclusions and jurisdiction. | Proposed: baseline — Review approved scope, electrical drawings, schedules and state regulatory requirements. | Proposed: baseline — Package covers only listed work [Fill: Installation scope]; relevant jurisdiction, system boundaries and exclusions are stated. | Guidance only; see Source Register: NSW-SIR-2025, CQA-ITP | Proposed: Once before installation; update on approved revision. | Proposed: electrical contractor/design reviewer. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical scope and compliance register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL02 | Personnel and approvals | Proposed: baseline — Check responsible electrical contractor/worker and required licences or authorisations are identified. | Proposed: baseline — Verify applicable jurisdiction licence/authorisation evidence and any network/inspection approval required for scope. | Proposed: baseline — Work is assigned to persons authorised for the work under applicable state rules; required inspection/certificate roles are identified. | Guidance only; see Source Register: ESV-COES, NSW-SIR-2025 | Proposed: Before work and when personnel/scope changes. | Proposed: Electrical contractor. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical personnel and approval register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL03 | Design and equipment submittal | Proposed: baseline — Review drawings, circuit schedules, equipment ratings, protective devices and approved substitutions. | Proposed: baseline — Check against approved design, specification, equipment schedules and coordination/interface documents. | Proposed: baseline — Installed design/equipment agrees with approved documents [Fill: Approved electrical drawings/schedules]/[Fill: Electrical specification/compliance pathway]; unresolved design conflicts are raised before installation. | Guidance only; see Source Register: CQA-ITP | Proposed: Each system/submittal and revision. | Proposed: electrical contractor submits; designer/client reviews as specified. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical design/submittal register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL04 | Incoming materials | Proposed: baseline — Check cables, accessories, enclosures and equipment identity, ratings, condition and traceability. | Proposed: baseline — Visual inspection; compare markings and delivery documents with approved schedule/submittal. | Proposed: baseline — Items match approved make/model/type/rating [Fill: Equipment/material submittals] and are undamaged, correctly identified and traceable. | Guidance only; see Source Register: CQA-ITP | Proposed: Each delivery/batch before installation. | Proposed: electrical contractor. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical materials register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL05 | Containment and supports | Proposed: baseline — Inspect conduits, trays, trunking, supports, segregation, routes and penetrations. | Proposed: baseline — Visual check and measure route/support details against drawings, specification, manufacturer instructions and fire/acoustic details where applicable. | Proposed: baseline — Route, support, segregation and penetrations match approved design [Fill: Approved electrical drawings/schedules] and applicable specified details; no unapproved interference or damage. | Guidance only; see Source Register: CQA-ITP | Proposed: Each area before cable pull and before concealment. | Proposed: electrical contractor. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Containment inspection checklist | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL06 | Concealed wiring | Proposed: baseline — Check cable type/size/route, protection, separation, identification and support before concealment. | Proposed: baseline — Visual inspection against approved circuit schedules and project requirements; photograph concealed work. | Proposed: baseline — Cable and installation details match approved schedule [Fill: Approved electrical drawings/schedules]/[Fill: Electrical specification/compliance pathway]; circuit identity and any required protection/separation are verified. | Guidance only; see Source Register: CQA-ITP | Proposed: Each area before concealment. | Proposed: electrical contractor; builder coordinates access. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Concealed electrical works checklist | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL07 | Cable installation and termination | Proposed: baseline — Inspect pulling, bend/routing condition, gland/termination, conductor identification and workmanship. | Proposed: baseline — Visual inspection against manufacturer instructions and approved equipment/circuit details. | Proposed: baseline — Cable installation and terminations are complete, undamaged, correctly identified and compatible with equipment instructions [Fill: Equipment/material submittals]/[Fill: Approved electrical drawings/schedules]. | Guidance only; see Source Register: CQA-ITP | Proposed: Each circuit/termination before energisation. | Proposed: electrical contractor. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Circuit installation checklist | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL08 | Switchboards and equipment mounting | Proposed: baseline — Check location, mounting, enclosure, access, identification and installed components. | Proposed: baseline — Visual/measured inspection against approved schedules, drawings and manufacturer data. | Proposed: baseline — Equipment location, enclosure, clearances/access, component schedule and identification match approved documents [Fill: Approved electrical drawings/schedules]/[Fill: Equipment/material submittals]; required covers/barriers fitted. | Guidance only; see Source Register: CQA-ITP | Proposed: Each board/equipment item before connection. | Proposed: electrical contractor; reviewer if specified. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Equipment installation checklist | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL09 | Earthing and bonding | Proposed: baseline — Check earthing/bonding conductors, connections, continuity provisions and labels per design. | Proposed: baseline — Visual verification and tests by appropriately licensed/authorised person using approved safe procedure and applicable standard. | Proposed: baseline — Earthing/bonding arrangement matches approved design and applicable adopted requirements [Fill: Verification/test requirements]; actual test results meet criteria confirmed by responsible electrician. Specific applicable acceptance: [Fill: Earthing/bonding verification criteria]. | Guidance only; see Source Register: NSW-TEST-SCHEDULE, NSW-SIR-2025 | Proposed: Each relevant circuit/system before energisation. | Proposed: Electrical contractor; verification by authorised electrical worker. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Earthing and bonding verification record | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL10 | Electrical installation verification | Proposed: baseline — Check required visual inspection and specified dead tests for completed installation. | Proposed: baseline — Only responsible licensed/authorised electrical worker performs tests using their approved safe method; record actual values and instrument. | Proposed: baseline — Specified tests are completed by authorised person and results meet project-adopted criteria [Fill: Verification/test requirements]; unresolved failures are corrected and retested. Specific applicable acceptance: [Fill: Installation verification criteria]. | Guidance only; see Source Register: NSW-TEST-SCHEDULE, NSW-SIR-2025, ESV-COES | Proposed: Each circuit/system before energisation and at specified stage. | Proposed: Licensed/authorised electrical worker. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical test results schedule | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL11 | Protective devices and settings | Proposed: baseline — Verify selected protective device identity, rating and approved settings. | Proposed: baseline — Compare installed item and settings with approved coordination/protection schedule; licensed worker verifies. | Proposed: baseline — Device and settings match approved design/schedule [Fill: Approved electrical drawings/schedules]; any variation has documented design approval. | Guidance only; see Source Register: CQA-ITP | Proposed: Each device/board before functional test. | Proposed: Electrical contractor; designer/protection engineer confirms settings where required. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Protective device/settings register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL12 | Functional and polarity checks | Proposed: baseline — Verify specified switching, polarity/circuit connection, phase sequence or functional operation as applicable. | Proposed: baseline — Authorised electrical worker follows applicable adopted procedure and records results; only perform tests in safe state. | Proposed: baseline — Specified functions and connection checks meet approved circuit/design requirements [Fill: Verification/test requirements]; record exceptions and retests. Specific applicable acceptance: [Fill: Connection and functional verification criteria]. | Guidance only; see Source Register: NSW-TEST-SCHEDULE, NSW-SIR-2025 | Proposed: Each applicable circuit/device during verification. | Proposed: Licensed/authorised electrical worker. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Functional test record | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL13 | RCD/protection functional testing | Proposed: baseline — Where included, verify specified device operation and record test particulars. | Proposed: baseline — Authorised person uses applicable adopted test method and specified criteria; distinguish commissioning verification from routine user pushbutton checks. | Proposed: baseline — Installed device and results meet specified circuit schedule and adopted verification criteria [Fill: Verification/test requirements]; no generic trip limits are inserted. Specific applicable acceptance: [Fill: Protective-device test criteria]. | Guidance only; see Source Register: NSW-TEST-SCHEDULE | Proposed: Each applicable device at specified verification stage. | Proposed: Licensed/authorised electrical worker. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | RCD/protection test schedule | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL14 | Defects and retesting | Proposed: baseline — Track nonconformances, corrective work and repeat verification. | Proposed: baseline — Record affected circuit/equipment, defect, authorised repair, retest results and revised status. | Proposed: baseline — Each nonconformance is closed against approved corrective action; failed affected tests are repeated and documented before release. | Guidance only; see Source Register: CQA-ITP | Proposed: Each defect/retest. | Proposed: Electrical contractor; reviewer per project. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical defect and retest register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL15 | Pre-energisation readiness | Proposed: baseline — Check covers, barriers, labels, test completion, approvals and interface prerequisites before energisation. | Proposed: baseline — Documented walkdown by responsible electrical contractor; verify statutory/network approvals and isolation/energisation plan. | Proposed: baseline — Required installation verification and approvals are complete; the responsible authorised person confirms safe prerequisites under applicable rules [Fill: Energisation/interface requirements]. | Guidance only; see Source Register: NSW-SIR-2025, ESV-COES | Proposed: Each board/system before energisation. | Proposed: Electrical contractor and authorised person; DNSP/ASP only within their authority. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Pre-energisation checklist | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL16 | Energisation and commissioning | Proposed: baseline — Record controlled energisation and specified system function/commissioning checks. | Proposed: baseline — Responsible authorised person records date, circuits/systems energised, checks and exceptions; follow approved switching arrangements. | Proposed: baseline — Energisation is authorised and specified commissioning functions meet approved design; exceptions are isolated and resolved. | Guidance only; see Source Register: NSW-SIR-2025 | Proposed: Each system/energisation event. | Proposed: Authorised electrical person; network provider where required. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Energisation and commissioning record | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |
| EL17 | Certificates and handover | Proposed: baseline — Verify required certificates, test reports, as-builts, schedules, product records and approvals. | Proposed: baseline — Review jurisdictional certificate requirements and contract handover index. | Proposed: baseline — Applicable certificates and records are issued by the required person and match installed scope; as-built circuit/equipment information is complete. | Guidance only; see Source Register: ESV-COES, NSW-SIR-2025 | Proposed: Once per package and after approved changes. | Proposed: Electrical contractor submits; builder compiles; regulator/inspector only as required. | TBC | Proposed: [Fill: reviewing role / authority assigned by project] | Proposed: Confirm required notice period, who receives notice, release authority and whether a contractual hold/witness point applies. | Electrical completion and handover register | Proposed: Check this baseline row against project documents; edit or remove it if it does not apply. |

## Inspection point key

Inspection point key: H = Proposed Hold Point - use only if assigned in the contract | W = Proposed Witness Point - use only if assigned in the contract | R = Proposed Review | S = Proposed Surveillance | TBC = To be confirmed | N/A = Not applicable. External H/W rights and whether work may proceed are governed by the project contract and approved process; proposed points require agreement.

# Blank Inspection Record Forms

[Fill: project name] | electrical-itp-template | Record actual observations during the work. No results or signatures are pre-filled.

| ITP ID / Stage | Inspection / method / acceptance | Location / lot | Date and result | Evidence / record ref. | Performed by / signature | Reviewed by / signature |
| --- | --- | --- | --- | --- | --- | --- |
| EL01 ¦ Scope and regulatory basis | Proposed: baseline — Confirm circuits, areas, system boundaries, exclusions and jurisdiction. Method: Proposed: baseline — Review approved scope, electrical drawings, schedules and state regulatory requirements. Accept when: Proposed: baseline — Package covers only listed work [Fill: Installation scope]; relevant jurisdiction, system boundaries and exclusions are stated. Record: Electrical scope and compliance register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL02 ¦ Personnel and approvals | Proposed: baseline — Check responsible electrical contractor/worker and required licences or authorisations are identified. Method: Proposed: baseline — Verify applicable jurisdiction licence/authorisation evidence and any network/inspection approval required for scope. Accept when: Proposed: baseline — Work is assigned to persons authorised for the work under applicable state rules; required inspection/certificate roles are identified. Record: Electrical personnel and approval register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL03 ¦ Design and equipment submittal | Proposed: baseline — Review drawings, circuit schedules, equipment ratings, protective devices and approved substitutions. Method: Proposed: baseline — Check against approved design, specification, equipment schedules and coordination/interface documents. Accept when: Proposed: baseline — Installed design/equipment agrees with approved documents [Fill: Approved electrical drawings/schedules]/[Fill: Electrical specification/compliance pathway]; unresolved design conflicts are raised before installation. Record: Electrical design/submittal register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL04 ¦ Incoming materials | Proposed: baseline — Check cables, accessories, enclosures and equipment identity, ratings, condition and traceability. Method: Proposed: baseline — Visual inspection; compare markings and delivery documents with approved schedule/submittal. Accept when: Proposed: baseline — Items match approved make/model/type/rating [Fill: Equipment/material submittals] and are undamaged, correctly identified and traceable. Record: Electrical materials register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL05 ¦ Containment and supports | Proposed: baseline — Inspect conduits, trays, trunking, supports, segregation, routes and penetrations. Method: Proposed: baseline — Visual check and measure route/support details against drawings, specification, manufacturer instructions and fire/acoustic details where applicable. Accept when: Proposed: baseline — Route, support, segregation and penetrations match approved design [Fill: Approved electrical drawings/schedules] and applicable specified details; no unapproved interference or damage. Record: Containment inspection checklist |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL06 ¦ Concealed wiring | Proposed: baseline — Check cable type/size/route, protection, separation, identification and support before concealment. Method: Proposed: baseline — Visual inspection against approved circuit schedules and project requirements; photograph concealed work. Accept when: Proposed: baseline — Cable and installation details match approved schedule [Fill: Approved electrical drawings/schedules]/[Fill: Electrical specification/compliance pathway]; circuit identity and any required protection/separation are verified. Record: Concealed electrical works checklist |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL07 ¦ Cable installation and termination | Proposed: baseline — Inspect pulling, bend/routing condition, gland/termination, conductor identification and workmanship. Method: Proposed: baseline — Visual inspection against manufacturer instructions and approved equipment/circuit details. Accept when: Proposed: baseline — Cable installation and terminations are complete, undamaged, correctly identified and compatible with equipment instructions [Fill: Equipment/material submittals]/[Fill: Approved electrical drawings/schedules]. Record: Circuit installation checklist |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL08 ¦ Switchboards and equipment mounting | Proposed: baseline — Check location, mounting, enclosure, access, identification and installed components. Method: Proposed: baseline — Visual/measured inspection against approved schedules, drawings and manufacturer data. Accept when: Proposed: baseline — Equipment location, enclosure, clearances/access, component schedule and identification match approved documents [Fill: Approved electrical drawings/schedules]/[Fill: Equipment/material submittals]; required covers/barriers fitted. Record: Equipment installation checklist |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL09 ¦ Earthing and bonding | Proposed: baseline — Check earthing/bonding conductors, connections, continuity provisions and labels per design. Method: Proposed: baseline — Visual verification and tests by appropriately licensed/authorised person using approved safe procedure and applicable standard. Accept when: Proposed: baseline — Earthing/bonding arrangement matches approved design and applicable adopted requirements [Fill: Verification/test requirements]; actual test results meet criteria confirmed by responsible electrician. Specific applicable acceptance: [Fill: Earthing/bonding verification criteria]. Record: Earthing and bonding verification record |  | Date: __________ Circuit/equipment ID: __________ Test method/reference: __________ Instrument ID: __________ Calibration due/date: __________ Measured result: __________ Unit: __________ Acceptance criterion reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL10 ¦ Electrical installation verification | Proposed: baseline — Check required visual inspection and specified dead tests for completed installation. Method: Proposed: baseline — Only responsible licensed/authorised electrical worker performs tests using their approved safe method; record actual values and instrument. Accept when: Proposed: baseline — Specified tests are completed by authorised person and results meet project-adopted criteria [Fill: Verification/test requirements]; unresolved failures are corrected and retested. Specific applicable acceptance: [Fill: Installation verification criteria]. Record: Electrical test results schedule |  | Date: __________ Circuit ID: __________ Test type: __________ Method/reference: __________ Instrument ID: __________ Actual reading: __________ Unit: __________ Criterion source/location: __________ Pass/fail/exception: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL11 ¦ Protective devices and settings | Proposed: baseline — Verify selected protective device identity, rating and approved settings. Method: Proposed: baseline — Compare installed item and settings with approved coordination/protection schedule; licensed worker verifies. Accept when: Proposed: baseline — Device and settings match approved design/schedule [Fill: Approved electrical drawings/schedules]; any variation has documented design approval. Record: Protective device/settings register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL12 ¦ Functional and polarity checks | Proposed: baseline — Verify specified switching, polarity/circuit connection, phase sequence or functional operation as applicable. Method: Proposed: baseline — Authorised electrical worker follows applicable adopted procedure and records results; only perform tests in safe state. Accept when: Proposed: baseline — Specified functions and connection checks meet approved circuit/design requirements [Fill: Verification/test requirements]; record exceptions and retests. Specific applicable acceptance: [Fill: Connection and functional verification criteria]. Record: Functional test record |  | Date: __________ Circuit/device ID: __________ Function/test: __________ Method/reference: __________ Instrument ID: __________ Actual reading: __________ Unit: __________ Outcome/exception: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL13 ¦ RCD/protection functional testing | Proposed: baseline — Where included, verify specified device operation and record test particulars. Method: Proposed: baseline — Authorised person uses applicable adopted test method and specified criteria; distinguish commissioning verification from routine user pushbutton checks. Accept when: Proposed: baseline — Installed device and results meet specified circuit schedule and adopted verification criteria [Fill: Verification/test requirements]; no generic trip limits are inserted. Specific applicable acceptance: [Fill: Protective-device test criteria]. Record: RCD/protection test schedule |  | Date: __________ Device ID: __________ Test type: __________ Instrument ID: __________ Measured value: __________ Unit: __________ Criterion source/location: __________ Pass/fail/exception: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL14 ¦ Defects and retesting | Proposed: baseline — Track nonconformances, corrective work and repeat verification. Method: Proposed: baseline — Record affected circuit/equipment, defect, authorised repair, retest results and revised status. Accept when: Proposed: baseline — Each nonconformance is closed against approved corrective action; failed affected tests are repeated and documented before release. Record: Electrical defect and retest register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL15 ¦ Pre-energisation readiness | Proposed: baseline — Check covers, barriers, labels, test completion, approvals and interface prerequisites before energisation. Method: Proposed: baseline — Documented walkdown by responsible electrical contractor; verify statutory/network approvals and isolation/energisation plan. Accept when: Proposed: baseline — Required installation verification and approvals are complete; the responsible authorised person confirms safe prerequisites under applicable rules [Fill: Energisation/interface requirements]. Record: Pre-energisation checklist |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL16 ¦ Energisation and commissioning | Proposed: baseline — Record controlled energisation and specified system function/commissioning checks. Method: Proposed: baseline — Responsible authorised person records date, circuits/systems energised, checks and exceptions; follow approved switching arrangements. Accept when: Proposed: baseline — Energisation is authorised and specified commissioning functions meet approved design; exceptions are isolated and resolved. Record: Energisation and commissioning record |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |
| EL17 ¦ Certificates and handover | Proposed: baseline — Verify required certificates, test reports, as-builts, schedules, product records and approvals. Method: Proposed: baseline — Review jurisdictional certificate requirements and contract handover index. Accept when: Proposed: baseline — Applicable certificates and records are issued by the required person and match installed scope; as-built circuit/equipment information is complete. Record: Electrical completion and handover register |  | Date: __________ Actual result/observation: __________ Evidence/photo/report reference: __________ Result / disposition: __________ Corrective action / retest ref.: __________ |  |  |  |

# Source Register

| Source ID | Title / filename | Revision | Type | Path / URL |
| --- | --- | --- | --- | --- |
| NSW-SIR-2025 | NSW Government, Service and Installation Rules (June 2025 issue surfaced in search; current issue must be checked) | See linked source; verify current edition and project adoption | guidance | https://www.energy.nsw.gov.au/nsw-plans-and-progress/regulation-and-policy/service-and-installation-rules |
| NSW-TEST-SCHEDULE | SafeWork NSW, Schedule of test results form | See linked source; verify current edition and project adoption | guidance | https://www.safework.nsw.gov.au/__data/assets/pdf_file/0018/1411920/Schedule_of_test_results.pdf |
| ESV-COES | Energy Safe Victoria, Certificates of Electrical Safety for consumers (reviewed September 2026) | See linked source; verify current edition and project adoption | guidance | https://www.energysafe.vic.gov.au/certificates-electrical-safety/certificates-electrical-safety-consumers |
| NSW-SIR-CURRENT | NSW Government, Service and Installation Rules current-edition page | See linked source; verify current edition and project adoption | guidance | https://www.energy.nsw.gov.au/nsw-plans-and-progress/regulation-and-policy/service-and-installation-rules |
| CQA-ITP | Construction Quality Association, Guide: How to create an ITP | See linked source; verify current edition and project adoption | guidance | https://www.cqa.org.au/post/guide-how-to-create-an-inspection-and-test-plan-itp |

# Open Confirmations

| Issue ID | Priority | ITP rows | Open item | Action needed |
| --- | --- | --- | --- | --- |
| CONF-001 | confirmation | EL01 | EL01: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-002 | confirmation | EL02 | EL02: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-003 | confirmation | EL03 | EL03: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-004 | confirmation | EL04 | EL04: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-005 | confirmation | EL05 | EL05: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-006 | confirmation | EL06 | EL06: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-007 | confirmation | EL07 | EL07: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-008 | confirmation | EL08 | EL08: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-009 | confirmation | EL09 | EL09: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-010 | confirmation | EL10 | EL10: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-011 | confirmation | EL11 | EL11: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-012 | confirmation | EL12 | EL12: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-013 | confirmation | EL13 | EL13: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-014 | confirmation | EL14 | EL14: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-015 | confirmation | EL15 | EL15: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-016 | confirmation | EL16 | EL16: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |
| CONF-017 | confirmation | EL17 | EL17: verify scope and project-specific requirements for this proposed baseline row. | Check current contract, drawings, specification, approved method, adopted standards and assigned roles; edit or delete this row as needed. |