Sanitary Drainage Installation ITP Template
Original editable baseline for ordinary building sanitary drainage pipework and connections. Covers approved route/connection, products, trench and bedding, actual invert/gradient checks, joints, pre-cover inspection, specified watertightness test, backfill protection and handover. Excludes sanitary fixture fit-off, liquid trade waste, vacuum systems, onsite wastewater, sewer authority mains and stormwater. Test criteria, falls, authorities and inspection notices must come from the applicable adopted code, approved design and project documents.
	Project
	[Enter project / state / parties]

	Package
	sanitary-drainage

	Document / revision
	[Enter controlled number and revision]

	Issue purpose
	For review - proposed editable baseline

	Boundary
	Complete against project documents; remove out-of-scope activities.


Read before use
This is a reusable proposed baseline, not an approved project plan or completed inspection record.
Enter actual acceptance criteria, source revisions/locators, lot basis, frequency, roles and contractual control points from the project. No numeric limit, test result, qualification, signature or client release has been supplied.
Confirm scope and remove or mark conditional rows that do not apply. Resolve missing or conflicting decisions with the assigned project authority.
Complete the matching blank Record Prompts only when actual work occurs; retain source certificates and original specialist reports.
Project inputs to resolve
Jurisdiction and authority basis: [Enter project source / decision] State/territory, local plumbing regulator and applicable adoption/variations. Confirm current legal requirements.
Approved service drawings and revisions: [Enter project source / decision] Identify plans, risers/isometrics, schedules, details and any approved design revisions.
Project specification and adopted standards: [Enter project source / decision] Record exact contract sources, revisions and adopted editions; do not assume the current edition is the contract edition.
Approved product and material schedule: [Enter project source / decision] Identify approved pipe, fittings, joints, valves and product evidence applicable to this service.
Licensed roles, inspections and release authority: [Enter project source / decision] Identify performing/reviewing roles, regulatory inspections, notification, contractual H/W points and release authority.
Project records and handover requirements: [Enter project source / decision] Identify required test sheets, as-builts, certificates, commissioning and dossier index.
Project-specific test method and acceptance: [Enter project source / decision] Enter method, test medium, limits, duration, section/lot and source from applicable standard/specification/authority.
Concealment, cover and access requirements: [Enter project source / decision] Identify project-required pre-cover evidence and inspection/release arrangements.
Design levels, gradients and hydraulic criteria: [Enter project source / decision] Enter approved invert/cover/finished levels, gradients, capacity and outfall conditions by drawing/spec reference.
Service boundaries and connection interfaces: [Enter project source / decision] Identify property connection, downstream/upstream party, utility/network owner and excluded systems.
Sanitary drainage design and authority basis: [Enter project source / decision] Identify approved alignment, fixture connections, gradients, invert levels, point of connection and regulator requirements.


Inspection and Test Plan
Proposed baseline. Replace prompts with controlled project criteria and references before project review.
SAN-01 · Drainage design and property connection
	Inspection / test
	Confirm system boundary, approved drainage arrangement and point of connection before setting out.

	Method
	Compare sanitary drainage plans, fixture schedule, invert/connection details and regulator/utility conditions; separate sanitary drainage from stormwater and excluded trade waste/on-site wastewater.

	Acceptance condition
	Only approved routes and connection details are used; capacity/design assumptions, authority conditions and unresolved interfaces are referred to the responsible designer. Project basis: [Enter Sanitary drainage design and authority basis]; [Enter Jurisdiction and authority basis].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage design and connection register

	Applicability / remarks
	Core for conventional building sanitary drainage. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-02 · Incoming pipe, fitting and access component check
	Inspection / test
	Check pipe, fittings, access points and chambers against approved schedule before installation.

	Method
	Match material, diameter/designation, joint type, access component and required product evidence to submittals; inspect delivery condition and identify segregated items.

	Acceptance condition
	Supplied components agree with approved material schedule and are fit for intended location/service; nonconforming items are held for disposition. Project basis: [Enter Approved product and material schedule]; [Enter Project specification and adopted standards].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage product and delivery register

	Applicability / remarks
	When products are supplied for installation. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-03 · Trench, bedding and support before laying
	Inspection / test
	Check prepared trench/support conditions before pipe placement.

	Method
	Inspect formation, bedding/support and interface clearances against the approved details and civil/structural coordination; record unsuitable ground, water or clashes for disposition.

	Acceptance condition
	Foundation and support arrangement match project details and any geotechnical/civil constraints; unresolved conditions are corrected or formally dispositioned before laying. Project basis: [Enter Approved service drawings and revisions]; [Enter Project specification and adopted standards].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage trench and bedding inspection

	Applicability / remarks
	Where drainage is installed in trench or supported construction. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-04 · Alignment, gradients, invert levels and fixture branches
	Inspection / test
	Verify installed route, branch connections and levels against approved drainage design before cover.

	Method
	Survey/measure the installed section and compare actual line, invert levels, gradients, fixture branches and cleanout/access positions to approved drawings and project tolerances.

	Acceptance condition
	Measured installation matches approved route and specified levels/gradients and maintains required access; no generic falls or tolerance values are supplied. Project basis: [Enter Sanitary drainage design and authority basis]; [Enter Design levels, gradients and hydraulic criteria]; [Enter Project specification and adopted standards].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage set-out and as-laid survey

	Applicability / remarks
	Before concealment for buried or inaccessible sections. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-05 · Joint assembly and contamination prevention
	Inspection / test
	Inspect joints, penetrations and pipe ends while visible, and confirm separation from stormwater.

	Method
	Check joint preparation/assembly against product instructions; inspect seals, support, connection direction, capped ends and cross-connections; record repairs before cover.

	Acceptance condition
	Joint assembly and routing follow approved system details and product instructions; sanitary and stormwater systems remain correctly separated; defects are closed before concealment. Project basis: [Enter Approved product and material schedule]; [Enter Approved service drawings and revisions].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage joint and separation check

	Applicability / remarks
	For installed joints and system interfaces. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-06 · Pre-cover inspection and test readiness
	Inspection / test
	Confirm the full test section is visible, accessible, isolated as needed and ready for the approved test before backfill or enclosure.

	Method
	Walk line and inspection points; reconcile section boundaries and test procedure; check connections/plugs and authority notice or inspection requirement before concealment.

	Acceptance condition
	Specified pre-cover inspections and notices are complete; each test section is identifiable and testable before concealment. WA bulletin is jurisdiction-specific and does not create a universal authority requirement. Project basis: [Enter Concealment, cover and access requirements]; [Enter Project-specific test method and acceptance]; [Enter Licensed roles, inspections and release authority].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage pre-cover and test readiness record

	Applicability / remarks
	Before backfill or concealment where the system will become inaccessible. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-07 · Specified watertightness test and retest
	Inspection / test
	Record the approved test on each identified section and track any repair/retest.

	Method
	Perform only the approved project/jurisdiction method; log test medium/setup, section, instrument if applicable, actual result and defects; repair and retest to the cited procedure.

	Acceptance condition
	Test result meets project-adopted criteria and regulatory pathway; a failed section remains open until accepted retest evidence exists. No WA test parameters are applied outside confirmed WA scope. Project basis: [Enter Project-specific test method and acceptance]; [Enter Jurisdiction and authority basis].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage test and retest certificate

	Applicability / remarks
	When test required by the project and jurisdiction. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-08 · Backfill, reinstatement and access protection
	Inspection / test
	Verify approved pipe protection, surround/backfill sequence and access points before the work is covered.

	Method
	Observe installation against civil details; verify required surround, marker/identification, compaction interface and access lids/cleanouts remain located and protected; record levels/areas.

	Acceptance condition
	Work complies with approved construction details and access remains usable; backfill or compaction does not proceed over unresolved inspection/test items. Project basis: [Enter Concealment, cover and access requirements]; [Enter Approved service drawings and revisions].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage backfill release and location record

	Applicability / remarks
	Where buried drainage is backfilled. Proposed baseline. Confirm applicability and replace with controlled project requirement.





SAN-09 · Connection, flow checks and handover
	Inspection / test
	Verify approved downstream connection, access and required completion notifications and records.

	Method
	Reconcile tie-in approval, inspection/test certificates, as-laid survey, defects, regulator notice/certificate and dossier index; perform only project-specified operational/flow checks.

	Acceptance condition
	Connection and required records match approved documents and local requirements; unresolved authority conditions or defects remain explicit at handover. Project basis: [Enter Sanitary drainage design and authority basis]; [Enter Licensed roles, inspections and release authority]; [Enter Project records and handover requirements].

	Reference / locator
	Topic guidance only; see Source Register. Enter the actual project document, revision and locator.

	Trigger / frequency
	Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing.

	Responsibility
	Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority]

	Point / external party
	TBC; Proposed: [Enter project-assigned reviewing / release authority]

	Notice / release
	Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned.

	Record
	Sanitary drainage completion and handover dossier

	Applicability / remarks
	Core where applicable to the project and jurisdiction. Proposed baseline. Confirm applicability and replace with controlled project requirement.





Blank matching record prompts
Complete the actual date, observation, result and responsible roles during the work. Blank cells are intentional; this template contains no completed inspection or approval.
SAN-01 · Drainage design and property connection
	Field
	Actual entry / evidence

	System / catchment ID
	

	Drawing and revision
	

	Point of connection reference
	

	Open design / approval item
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-02 · Incoming pipe, fitting and access component check
	Field
	Actual entry / evidence

	Pipe / fitting / access item
	

	Location / service
	

	Submittal / product evidence
	

	Condition / disposition
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-03 · Trench, bedding and support before laying
	Field
	Actual entry / evidence

	Trench / chainage
	

	Detail / revision
	

	Observed formation and support
	

	Ground / clash / instruction ref.
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-04 · Alignment, gradients, invert levels and fixture branches
	Field
	Actual entry / evidence

	Section / chainage
	

	Actual invert levels
	

	Actual gradient / method
	

	Drawing / tolerance reference
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-05 · Joint assembly and contamination prevention
	Field
	Actual entry / evidence

	Section / location
	

	Joint / product type
	

	System identification / separation
	

	Defect / repair reference
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-06 · Pre-cover inspection and test readiness
	Field
	Actual entry / evidence

	Test section / location
	

	Inspection / notice reference
	

	Approved test procedure
	

	Release / open item reference
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-07 · Specified watertightness test and retest
	Field
	Actual entry / evidence

	Test section
	

	Method / source
	

	Actual result / observation
	

	Repair and retest reference
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-08 · Backfill, reinstatement and access protection
	Field
	Actual entry / evidence

	Section / chainage
	

	Surround / backfill reference
	

	Access point / lid check
	

	Inspection / release record
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





SAN-09 · Connection, flow checks and handover
	Field
	Actual entry / evidence

	Connection / approval reference
	

	Notice / certificate
	

	As-laid drawing / survey
	

	Open item / owner
	

	Date / location / lot
	

	Actual observation / result / unit
	

	Original evidence / report reference
	

	Disposition / corrective action / recheck
	

	Performed by / date
	

	Reviewed / decision reference
	





Topic guidance sources and limitations
Australian Building Codes Board, NCC 2022 Volume Three — Plumbing Code of Australia
Accessed 2026-10-07; Volume Three index: Section B Water services, Section C Sanitary plumbing and drainage systems, state/territory schedules and Schedule 2 referenced documents.
https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three
Official national framework and source locator. State adoption, variations, application and project compliance pathway must be confirmed; NCC edition is not assumed to be the contract edition.
Australian Building Codes Board, NCC 2022 Volume Three — Schedule 2 Referenced documents
Accessed 2026-10-07; entries AS/NZS 3500 Part 1:2021 (B1D3 etc.), Part 2:2021 (C1/C2 provisions) and Part 3:2021 (F1D3, H2D2/H2D6 and 7.4.3).
https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three/2-referenced-documents/referenced-documents
Confirms NCC 2022 referenced-document editions and provision cross-references only. Verify the edition actually adopted by the project jurisdiction and contract; full standards text was not used.
Australian Building Codes Board, NCC 2022 Volume Three — Part C1 Sanitary plumbing systems
Accessed 2026-10-07; introduction and Performance Requirements C1P1 disposal, C1P2 access, C1P4 uncontrolled discharge, C1P6 contamination, C1P7 damage.
https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three/c-sanitary-plumbing-and-drainage-systems/part-c1-sanitary-plumbing-systems
Official scope and outcome framework for sanitary plumbing; no generic project acceptance values or inspection frequencies inferred.
Australian Building Codes Board, NCC 2022 Volume Three — Part C2 Sanitary drainage systems
Accessed 2026-10-07; C2 provisions for sanitary drainage performance and pressure testing; installation design remains tied to applicable code pathway and referenced documents.
https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three/c-sanitary-plumbing-and-drainage-systems/part-c2-sanitary-drainage-systems
Official sanitary drainage scope and testing/design pathway locator. Check jurisdiction adoption and approved project design; no universal values copied into the baseline.
Government of Western Australia, Industry Bulletin 133 — Sanitary plumbing and sanitary drainage installation testing
Accessed 2026-10-07; official bulletin page and linked PDF inspected. Bulletin describes WA testing and notification requirements, test before backfill and repair/retest sequence; PDF pp. 1–2.
https://www.wa.gov.au/government/publications/industry-bulletin-133-sanitary-plumbing-and-drainage-installation-testing
Specific WA example supporting test-before-concealment, defect repair/retest and authority notification as topics. Do not transfer WA legal methods, numeric criteria or notification duties to other jurisdictions.
Topic guidance is provided for orientation only. Confirm applicable jurisdictional adoption, approved design and contract requirements. No cited source substitutes for the complete controlled project documents or licensed standards.
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