# Water Services Installation ITP Template

Original editable baseline for ordinary building cold-water, heated-water and non-drinking water service pipework where selected. Covers product evidence, service routing, jointing, project-specified testing, conditional flushing/disinfection, operational checks and handover. Excludes fire-fighting, gas, process/high-pressure, HVAC, pools, off-site utility mains and specialist treatment plant. System selection and all numeric criteria must come from applicable authority, approved design and contract.

| Project | [Enter project / state / parties] |
| --- | --- |
| Package | water-services |
| Document / revision | [Enter controlled number and revision] |
| Issue purpose | For review - proposed editable baseline |
| Boundary | Complete against project documents; remove out-of-scope activities. |

# Read before use

This is a reusable proposed baseline, not an approved project plan or completed inspection record.

Enter actual acceptance criteria, source revisions/locators, lot basis, frequency, roles and contractual control points from the project. No numeric limit, test result, qualification, signature or client release has been supplied.

Confirm scope and remove or mark conditional rows that do not apply. Resolve missing or conflicting decisions with the assigned project authority.

Complete the matching blank Record Prompts only when actual work occurs; retain source certificates and original specialist reports.

# Project inputs to resolve

Jurisdiction and authority basis: [Enter project source / decision] State/territory, local plumbing regulator and applicable adoption/variations. Confirm current legal requirements.

Approved service drawings and revisions: [Enter project source / decision] Identify plans, risers/isometrics, schedules, details and any approved design revisions.

Project specification and adopted standards: [Enter project source / decision] Record exact contract sources, revisions and adopted editions; do not assume the current edition is the contract edition.

Approved product and material schedule: [Enter project source / decision] Identify approved pipe, fittings, joints, valves and product evidence applicable to this service.

Licensed roles, inspections and release authority: [Enter project source / decision] Identify performing/reviewing roles, regulatory inspections, notification, contractual H/W points and release authority.

Project records and handover requirements: [Enter project source / decision] Identify required test sheets, as-builts, certificates, commissioning and dossier index.

Project-specific test method and acceptance: [Enter project source / decision] Enter method, test medium, limits, duration, section/lot and source from applicable standard/specification/authority.

Service boundaries and connection interfaces: [Enter project source / decision] Identify property connection, downstream/upstream party, utility/network owner and excluded systems.

Flushing, disinfection and water quality requirements: [Enter project source / decision] Confirm whether required for this system and identify approved procedure, limits, sampling and disposal.

# Inspection and Test Plan

Proposed baseline. Replace prompts with controlled project criteria and references before project review.

## WTR-01 · Service boundary and design release

| Inspection / test | Confirm the included cold, heated and non-drinking water systems, tie-in points and work boundaries before installation. |
| --- | --- |
| Method | Compare approved service drawings, schedules, scope and interface register; distinguish potable/non-potable, cold/heated services, utility work and excluded fire/process systems. |
| Acceptance condition | Only identified services and current approved drawings are released; unresolved design, cross-connection or point-of-connection decisions are recorded for the responsible designer/authority. Project basis: [Enter Approved service drawings and revisions]; [Enter Service boundaries and connection interfaces]; [Enter Jurisdiction and authority basis]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water service scope and interface register |
| Applicability / remarks | Core for water-service package. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-02 · Product approval and delivery check

| Inspection / test | Check pipe, fittings, valves and devices against the approved service schedule and applicable evidence-of-suitability requirements. |
| --- | --- |
| Method | Match product identity, size/material, pressure/service designation and required certification/document references to approved submittals; segregate mismatched or damaged products. |
| Acceptance condition | Products match approved project schedule and required evidence is available for the intended service and jurisdiction. No product approval is inferred from this template. Project basis: [Enter Approved product and material schedule]; [Enter Project specification and adopted standards]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water product receipt and approval register |
| Applicability / remarks | When water-service products are supplied for installation. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-03 · Set-out, support and service separation

| Inspection / test | Verify installed route, identification and supports against approved drawings and service coordination before concealment. |
| --- | --- |
| Method | Walk the installed section; compare route, levels/clearances, support details, sleeves and service identification to controlled drawings and coordination requirements; record deviations. |
| Acceptance condition | Installed route and support/interface details agree with approved documents; separation, access and identification requirements are resolved from project sources. Project basis: [Enter Approved service drawings and revisions]; [Enter Project specification and adopted standards]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water service installation and pre-cover record |
| Applicability / remarks | Where concealed or supported water pipework is installed. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-04 · Jointing and concealed workmanship

| Inspection / test | Inspect completed joints and fittings while accessible, before insulation or enclosure. |
| --- | --- |
| Method | Verify joint type and installer/process evidence against manufacturer instructions and approved method; visually inspect accessible joints and record defects and repair references. |
| Acceptance condition | Jointing method and workmanship meet approved product instructions and project criteria; all identified defects are dispositioned before concealment. Project basis: [Enter Approved product and material schedule]; [Enter Project specification and adopted standards]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water joint and pre-concealment inspection log |
| Applicability / remarks | For installed joints that will become inaccessible. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-05 · Pressure test readiness and isolation

| Inspection / test | Confirm each test section, boundaries, compatible test setup and protection of connected components before testing. |
| --- | --- |
| Method | Review approved test procedure; verify section limits, gauge/instrument identification and calibration status if required, isolated appliances, test medium and safety controls. |
| Acceptance condition | Test section and procedure match project-approved test plan and applicable service requirements; vulnerable components are protected and setup is recorded before pressurisation. Project basis: [Enter Project-specific test method and acceptance]; [Enter Project specification and adopted standards]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water pressure test setup record |
| Applicability / remarks | When a pressure test is specified for the installed service. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-06 · Pressure test and defect closeout

| Inspection / test | Record the specified water-service test result and verify repair/retest evidence where required. |
| --- | --- |
| Method | Perform the approved test for the defined section; record actual medium, set conditions, start/end readings, times, observed leakage and test instrument; repair and repeat per approved procedure. |
| Acceptance condition | Actual results satisfy only the project-approved acceptance criteria and authority pathway; failed tests remain open until documented repair and accepted retest. Do not apply WA example values unless expressly adopted. Project basis: [Enter Project-specific test method and acceptance]; [Enter Jurisdiction and authority basis]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water service test and retest certificate |
| Applicability / remarks | When the specified test is applicable. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-07 · Flushing and disinfection, where required

| Inspection / test | Determine and complete project-required flushing, disinfection and water-quality checks before service use. |
| --- | --- |
| Method | Confirm system type, scope and written procedure; flush/disinfect only where required and by approved method; record water quality samples/results, disposal and clearance where specified. |
| Acceptance condition | Applicable flushing/disinfection and water-quality evidence meets authority and project requirements; where not required, the basis is recorded. No universal disinfection trigger, dose or residual is supplied. Project basis: [Enter Flushing, disinfection and water quality requirements]; [Enter Jurisdiction and authority basis]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water flushing, disinfection and sampling record |
| Applicability / remarks | Conditional on service type, jurisdiction and project procedure. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-08 · Operational checks and service identification

| Inspection / test | Check completed valves, outlets, controls, labels and access against approved schedules and operation requirements. |
| --- | --- |
| Method | Operate each scheduled item; verify intended service identification, access/isolation, flow direction and documented function; record exceptions and closeout actions. |
| Acceptance condition | Installed items match approved schedule and perform as specified; access and service identification are maintained and defects are closed. Project basis: [Enter Approved service drawings and revisions]; [Enter Project specification and adopted standards]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water service functional check and asset register |
| Applicability / remarks | At completion for included water services. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

## WTR-09 · Regulatory inspection and handover

| Inspection / test | Confirm required authority notifications, inspection outcomes and service records are complete for handover. |
| --- | --- |
| Method | Reconcile regulator/utility approvals, certificates, approved deviations, test/flush results, marked-up drawings and operation information against the project dossier index. |
| Acceptance condition | All required project and jurisdiction records are indexed; outstanding authority conditions, defects or exclusions are visible and not represented as accepted. Project basis: [Enter Licensed roles, inspections and release authority]; [Enter Project records and handover requirements]. |
| Reference / locator | Topic guidance only; see Source Register. Enter the actual project document, revision and locator. |
| Trigger / frequency | Proposed: At the identified item / lot before the next step that would obscure or change the evidence; confirm project-defined coverage and timing. |
| Responsibility | Proposed: Assigned licensed plumbing contractor performs and records; reviewer / regulator acts only within documented authority. Project role basis: [Enter Licensed roles, inspections and release authority] |
| Point / external party | TBC; Proposed: [Enter project-assigned reviewing / release authority] |
| Notice / release | Proposed: Confirm project notice recipient, evidence, timing and release authority; no external control point is assigned. |
| Record | Water services commissioning and handover dossier index |
| Applicability / remarks | Core where required by contract or authority. Proposed baseline. Confirm applicability and replace with controlled project requirement. |

# Blank matching record prompts

Complete the actual date, observation, result and responsible roles during the work. Blank cells are intentional; this template contains no completed inspection or approval.

## WTR-01 · Service boundary and design release

| Field | Actual entry / evidence |
| --- | --- |
| Service/system ID |  |
| Drawing and revision |  |
| Tie-in / work boundary |  |
| Open decision reference |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-02 · Product approval and delivery check

| Field | Actual entry / evidence |
| --- | --- |
| Product / component |  |
| Service and location |  |
| Approval / certification reference |  |
| Condition / disposition |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-03 · Set-out, support and service separation

| Field | Actual entry / evidence |
| --- | --- |
| Section / location |  |
| Drawing and revision |  |
| Support / restraint reference |  |
| Deviation / RFI reference |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-04 · Jointing and concealed workmanship

| Field | Actual entry / evidence |
| --- | --- |
| Section / location |  |
| Joint type / installer |  |
| Observation / defect |  |
| Repair / reinspection reference |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-05 · Pressure test readiness and isolation

| Field | Actual entry / evidence |
| --- | --- |
| Test section |  |
| Procedure / revision |  |
| Gauge ID / calibration reference |  |
| Isolation and protection check |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-06 · Pressure test and defect closeout

| Field | Actual entry / evidence |
| --- | --- |
| Test section |  |
| Actual readings / result |  |
| Actual start/end time |  |
| Defect / repair / retest ref. |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-07 · Flushing and disinfection, where required

| Field | Actual entry / evidence |
| --- | --- |
| System / section |  |
| Approved procedure reference |  |
| Sample point / lab result |  |
| Clearance / disposition |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-08 · Operational checks and service identification

| Field | Actual entry / evidence |
| --- | --- |
| Valve / outlet / control ID |  |
| Location / service |  |
| Observed function |  |
| Defect / closeout reference |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

## WTR-09 · Regulatory inspection and handover

| Field | Actual entry / evidence |
| --- | --- |
| Record / certificate |  |
| Document number / revision |  |
| Status / authority |  |
| Open condition / owner |  |
| Date / location / lot |  |
| Actual observation / result / unit |  |
| Original evidence / report reference |  |
| Disposition / corrective action / recheck |  |
| Performed by / date |  |
| Reviewed / decision reference |  |

# Topic guidance sources and limitations

## Australian Building Codes Board, NCC 2022 Volume Three — Plumbing Code of Australia

Accessed 2026-10-07; Volume Three index: Section B Water services, Section C Sanitary plumbing and drainage systems, state/territory schedules and Schedule 2 referenced documents.

https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three

Official national framework and source locator. State adoption, variations, application and project compliance pathway must be confirmed; NCC edition is not assumed to be the contract edition.

## Australian Building Codes Board, NCC 2022 Volume Three — Schedule 2 Referenced documents

Accessed 2026-10-07; entries AS/NZS 3500 Part 1:2021 (B1D3 etc.), Part 2:2021 (C1/C2 provisions) and Part 3:2021 (F1D3, H2D2/H2D6 and 7.4.3).

https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three/2-referenced-documents/referenced-documents

Confirms NCC 2022 referenced-document editions and provision cross-references only. Verify the edition actually adopted by the project jurisdiction and contract; full standards text was not used.

## Australian Building Codes Board, NCC 2022 Volume Three — Section B Water services

Accessed 2026-10-07; index entries Part B1 Cold water services, B2 Heated water services, B3 Non-drinking water services, B5 Cross-connection control, B6 Rainwater services and B7 Rainwater storage.

https://ncc.abcb.gov.au/editions/ncc-2022/adopted/volume-three/b-water-services

Defines service group coverage and compliance topic routing; it does not set project-specific test methods, design values, hold points or blanket disinfection requirements.

## WA Plumbers Licensing Board, Pipe sizing and commissioning

Version 4, May 2023: page 4 Testing and commissioning of water services flowchart; page 5 WA scope and adopted-code notes. Checked 7 October 2026.

https://www.wa.gov.au/media/54256/download

WA-specific technical example only. Its stated pressure/time and disinfection triggers are intentionally not reproduced as generic criteria; use only if confirmed applicable by jurisdiction, contract and service design.

## ABCB WaterMark, What requires WaterMark?

Transcript: schedules of products/excluded products and matching certificate/product identity. Checked 7 October 2026.

https://watermark.abcb.gov.au/resources/videos/what-requires-watermark

Topic support for checking certification applicability and product identity; not every plumbing product requires WaterMark. No individual product or installation is certified by this template.

Topic guidance is provided for orientation only. Confirm applicable jurisdictional adoption, approved design and contract requirements. No cited source substitutes for the complete controlled project documents or licensed standards.